## fluidList
fluidName | rho_kgm3 | mu_mPas | Comment
water | 993.99 | 0.719 | 35 C, NIST
propane | 476.14 | 0.08745 | 35 C, NIST
Air_1 | 8.4736 | 0.017894 | 700 kPaa and 15 C, - low pressure viscosity

## hydraulics
Segment | Description | LineTag | PnID | NPS | Schedule | Material | fluidName | inletP_kPaa | massFlow
A | one line | L-001 | optional | 4 | STD | Commercial steel | water | 100 | 100000
B | another line | L-002 | optional | 8 | STD | Commercial steel | propane | 100 | 50000

## fittingList
Segment | fittingType | num_length_m | comment | revision
A | EL45-THD-STD | 2
A | PIPE | 55 | smurf | B
B | PIPE | 100

## fitting3K
fittingType | Description | Fitting | Type | Geometry | K1 | Kinf | Kd | Kp
PIPE | PIPE |  |  |  | 0 | 0 | 0 | 1
ELL-THD-STD | Elbow - 90 DegreeThreaded-Standardr/D = 1 | Elbow - 90 Degree | Threaded-Standard | r/D = 1 | 800 | 0.14 | 4 | 0
ELL-THD-LR | Elbow - 90 DegreeThreaded Long Radiusr/D = 1.5 | Elbow - 90 Degree | Threaded Long Radius | r/D = 1.5 | 800 | 0.071 | 4.2 | 0
ELL-FLG-RD1 | Elbow - 90 DegreeFlanged Welded Bendr/D = 1 | Elbow - 90 Degree | Flanged Welded Bend | r/D = 1 | 800 | 0.091 | 4 | 0
ELL-FLG-RD2 | Elbow - 90 DegreeFlanged Welded Bendr/D = 2 | Elbow - 90 Degree | Flanged Welded Bend | r/D = 2 | 800 | 0.056 | 3.9 | 0
ELL-FLG-RD4 | Elbow - 90 DegreeFlanged Welded Bendr/D = 4 | Elbow - 90 Degree | Flanged Welded Bend | r/D = 4 | 800 | 0.066 | 3.9 | 0
ELL-FLG-RD6 | Elbow - 90 DegreeFlanged Welded Bendr/D = 6 | Elbow - 90 Degree | Flanged Welded Bend | r/D = 6 | 800 | 0.075 | 4.2 | 0
ELL-MIT-1 | Elbow - 90 DegreeMitered 1 Weld 90 Degree | Elbow - 90 Degree | Mitered 1 Weld 90 Degree |  | 1000 | 0.27 | 4 | 0
ELL-MIT-2 | Elbow - 90 DegreeMitered 2 Welds 45 Degree | Elbow - 90 Degree | Mitered 2 Welds 45 Degree |  | 800 | 0.068 | 4.1 | 0
EL-MIT-3 | Elbow - 90 DegreeMitered 3 Welds 30 Degree | Elbow - 90 Degree | Mitered 3 Welds 30 Degree |  | 800 | 0.035 | 4.2 | 0
EL45-THD-STD | Elbow - 45 DegreeThreaded Standardr/D = 1 | Elbow - 45 Degree | Threaded Standard | r/D = 1 | 500 | 0.071 | 4.2 | 0
EL45-LR | Elbow - 45 DegreeLong Radiusr/D = 1.5 | Elbow - 45 Degree | Long Radius | r/D = 1.5 | 500 | 0.052 | 4 | 0
EL45-MIT-1 | Elbow - 45 DegreeMitered 1 Weld 45 Degree | Elbow - 45 Degree | Mitered 1 Weld 45 Degree |  | 500 | 0.086 | 4 | 0
EL45-MIT-2 | Elbow - 45 DegreeMitered 2 Welds 22.5 Degree | Elbow - 45 Degree | Mitered 2 Welds 22.5 Degree |  | 500 | 0.052 | 4 | 0
EL180-THD-1 | Elbows - 180 DegreeThreaded Close Return Bendr/D = 1 | Elbows - 180 Degree | Threaded Close Return Bend | r/D = 1 | 1000 | 0.23 | 4 | 0
EL180-FLG-RD1 | Elbows - 180 DegreeFlangedr/D = 1 | Elbows - 180 Degree | Flanged | r/D = 1 | 1000 | 0.12 | 4 | 0
EL180-FLG-RD15 | Elbows - 180 DegreeAllr/D = 1.5 | Elbows - 180 Degree | All | r/D = 1.5 | 1000 | 0.1 | 4 | 0
TEE-THD-RD1 | TEEThreadedr/D = 1 | TEE | Threaded | r/D = 1 | 500 | 0.274 | 4 | 0
TEE-THD-RD15 | TEEThreadedr/D = 1.5 | TEE | Threaded | r/D = 1.5 | 800 | 0.14 | 4 | 0
TEE-FLG | TEEFlangedr/D = 1 | TEE | Flanged | r/D = 1 | 800 | 0.28 | 4 | 0
TEE-STUB | TEEStub-in Branch | TEE | Stub-in Branch |  | 1000 | 0.34 | 4 | 0
TEE-THD-THRU | TEERun Through Threadedr/D = 1 | TEE | Run Through Threaded | r/D = 1 | 200 | 0.091 | 4 | 0
TEE-FLG-THRU | TEEFlangedr/D = 1 | TEE | Flanged | r/D = 1 | 150 | 0.017 | 4 | 0
TEE-STUB-THRU | TEEStub-in Branch | TEE | Stub-in Branch |  | 100 | 0 | 0 | 0
VALVE-ANGLE-45-FULL | ValveAngle - 45 DegreeFull Line Size b = 1 | Valve | Angle - 45 Degree | Full Line Size b = 1 | 950 | 0.25 | 4 | 0
VALVE-ANGLE-90-FULL | ValveAngle - 90 DegreeFull Line Size b = 1 | Valve | Angle - 90 Degree | Full Line Size b = 1 | 1000 | 0.69 | 4 | 0
VALVE-GLOBE-STD-B1 | ValveGlobeStandard b = 1 | Valve | Globe | Standard b = 1 | 1500 | 1.7 | 3.6 | 0
VALVE-PLUG-BRANCH | ValvePlugBranch Flow | Valve | Plug | Branch Flow | 500 | 0.41 | 4 | 0
VALVE-PLUG-THRU | ValvePlugStraight Through | Valve | Plug | Straight Through | 300 | 0.084 | 3.9 | 0
VALVE-PLUG-3WAY-THRU | ValvePlugThree-Way (flow through) | Valve | Plug | Three-Way (flow through) | 300 | 0.14 | 4 | 0
VALVE-GATE-STD-B1 | ValveGateStandard b = 1 | Valve | Gate | Standard b = 1 | 300 | 0.037 | 3.9 | 0
VALVE-BALL-STD-B1 | ValveBallStandard b = 1 | Valve | Ball | Standard b = 1 | 300 | 0.017 | 4 | 0
VALVE-DIAPH-DAM | ValveDiaphragmDam-Type | Valve | Diaphragm | Dam-Type | 1000 | 0.69 | 4.9 | 0
VALVE-CHECK-SWING | ValveSwing CheckVmin = 35r-1/2 | Valve | Swing Check | Vmin = 35r-1/2 | 1500 | 0.46 | 4 | 0
VALVE-CHECK-LIFT | ValveLift CheckVmin = 40r-1/2 | Valve | Lift Check | Vmin = 40r-1/2 | 2000 | 2.85 | 3.8 | 0
ENTRANCE-NON-RECOVER | InletNon-recoverable | Inlet |  | Non-recoverable | 0 | 1.5 | 0 | 0
EXIT-NON-RECOVER | ExitNon-recoverable | Exit |  | Non-recoverable | 0 | 0 | 0 | 0

## pipeRoughness
Material | roughnessMM
Drawn tubing | 0.0015
Plastic | 0.0015
Fiberglass | 0.005
Stainless steel | 0.015
Commercial steel | 0.068
Galvanized steel | 0.15
Rusted steel | 2.075
Riveted steel | 4.95
New cast iron | 0.53
Worn cast iron | 1.2
Corroding cast iron | 2
Galvanized iron | 0.015
Smoothed cement | 0.3
Ordinary concrete | 1.7

## pipeTable
NPS | STD | XS | XXS | SCH10 | SCH20 | SCH30 | SCH40 | SCH60 | SCH80 | SCH100 | SCH120 | SCH140 | SCH160
0.125 | 6.84 | 5.48 |  |  |  |  | 6.84 |  | 5.48
0.25 | 9.22 | 7.66 |  |  |  |  | 9.22 |  | 7.66
0.375 | 11.56 | 10.7 |  |  |  |  | 11.56 |  | 10.7
0.5 | 15.7 | 13.9 | 6.3 |  |  |  | 15.7 |  | 13.9 |  |  |  | 11.7
0.75 | 20.9 | 18.9 | 11.1 |  |  |  | 20.9 |  | 18.9 |  |  |  | 15.5
1 | 26.6 | 24.4 | 15.2 |  |  |  | 26.6 |  | 24.4 |  |  |  | 20.6
1.25 | 35 | 32.4 | 22.8 |  |  |  | 35 |  | 32.4 |  |  |  | 29.4
1.5 | 40.9 | 38.1 | 27.9 |  |  |  | 40.9 |  | 38.1 |  |  |  | 34.1
2 | 52.5 | 49.3 | 38.1 |  |  |  | 52.5 |  | 49.3 |  |  |  | 42.9
2.5 | 62.6 | 59 | 45 |  |  |  | 62.6 |  | 59 |  |  |  | 54
3 | 77.9 | 73.7 | 58.5 |  |  |  | 77.9 |  | 73.7 |  |  |  | 66.7
3.5 | 90.2 | 85.4 |  |  |  |  | 90.2 |  | 85.4
4 | 102.3 | 97.1 | 80.1 |  |  |  | 102.3 |  | 97.1 |  | 92.1 |  | 87.3
5 | 128.1 | 122.3 | 103.1 |  |  |  | 128.1 |  | 122.3 |  | 115.9 |  | 109.5
6 | 154.1 | 146.3 | 124.5 |  |  |  | 154.1 |  | 146.3 |  | 139.7 |  | 131.7
8 | 202.7 | 193.7 | 174.7 |  | 206.3 | 205.1 | 202.7 | 198.5 | 193.7 | 188.9 | 182.5 | 177.9 | 173.1
10 | 254.5 | 247.7 | 222.3 |  | 260.3 | 257.5 | 254.5 | 247.7 | 242.9 | 236.5 | 230.3 | 222.3 | 215.9
12 | 304.9 | 298.5 | 273.1 |  | 311.1 | 307.1 | 303.3 | 295.3 | 288.9 | 281.1 | 273.1 | 266.7 | 257.3
14 | 336.54 | 330.2 |  | 342.9 | 339.76 | 336.54 | 333.34 | 325.42 | 317.5 | 307.94 | 300.02 | 292.1 | 284.18
16 | 387.34 | 381 |  | 393.7 | 390.56 | 387.34 | 381 | 373.08 | 363.52 | 354.02 | 344.48 | 333.36 | 325.42
18 | 438.14 | 431.8 |  | 444.5 | 441.36 | 434.94 | 428.66 | 419.1 | 409.54 | 398.48 | 387.36 | 377.82 | 366.72
20 | 488.94 | 482.6 |  | 495.3 | 488.94 | 482.6 | 477.82 | 466.76 | 455.62 | 442.92 | 431.8 | 419.1 | 407.98
22 | 539.74 | 533.4 |  | 546.1 | 539.74 | 533.4 |  | 514.34 | 501.6
24 | 590.54 | 584.2 |  | 596.9 | 590.54 | 581.06 | 574.64 | 560.38 | 547.68 | 531.82 | 517.56 | 504.82 | 490.52
26 | 641.34 | 635 |  | 644.56 | 635 | 628.64
28 | 692.14 | 685.8 |  | 695.36 | 685.8 | 679.44
30 | 742.94 | 736.6 |  | 746.16 | 736.6 | 730.24
32 | 793.74 | 787.4 |  | 796.96 | 787.4 | 781.04 | 777.84
36 | 895.34 | 889 |  | 898.56 | 889 | 882.64 | 876.3
42 | 1047.74 | 1041.4
48 | 1200.14 | 1193.8

## pipeIDlist
NPS | Schedule | Idmm
0.125 | OD | 10.287
0.25 | OD | 13.716
0.375 | OD | 17.145
0.5 | OD | 21.336
0.75 | OD | 26.67
1 | OD | 33.401
1.25 | OD | 42.164
1.5 | OD | 48.26
2 | OD | 60.325
2.5 | OD | 73.025
3 | OD | 88.9
3.5 | OD | 101.6
4 | OD | 114.3
5 | OD | 141.3002
6 | OD | 168.275
8 | OD | 219.075
10 | OD | 273.05
12 | OD | 323.85
14 | OD | 355.6
16 | OD | 406.4
18 | OD | 457.2
20 | OD | 508
22 | OD | 558.8
24 | OD | 609.6
26 | OD | 660.4
28 | OD | 711.2
30 | OD | 762
32 | OD | 812.8
36 | OD | 914.4
42 | OD | 1066.8
48 | OD | 1219.2
0.125 | STD | 6.84
0.25 | STD | 9.22
0.375 | STD | 11.56
0.5 | STD | 15.7
0.75 | STD | 20.9
1 | STD | 26.6
1.25 | STD | 35
1.5 | STD | 40.9
2 | STD | 52.5
2.5 | STD | 62.6
3 | STD | 77.9
3.5 | STD | 90.2
4 | STD | 102.3
5 | STD | 128.1
6 | STD | 154.1
8 | STD | 202.7
10 | STD | 254.5
12 | STD | 304.9
14 | STD | 336.54
16 | STD | 387.34
18 | STD | 438.14
20 | STD | 488.94
22 | STD | 539.74
24 | STD | 590.54
26 | STD | 641.34
28 | STD | 692.14
30 | STD | 742.94
32 | STD | 793.74
36 | STD | 895.34
42 | STD | 1047.74
48 | STD | 1200.14
0.125 | XS | 5.48
0.25 | XS | 7.66
0.375 | XS | 10.7
0.5 | XS | 13.9
0.75 | XS | 18.9
1 | XS | 24.4
1.25 | XS | 32.4
1.5 | XS | 38.1
2 | XS | 49.3
2.5 | XS | 59
3 | XS | 73.7
3.5 | XS | 85.4
4 | XS | 97.1
5 | XS | 122.3
6 | XS | 146.3
8 | XS | 193.7
10 | XS | 247.7
12 | XS | 298.5
14 | XS | 330.2
16 | XS | 381
18 | XS | 431.8
20 | XS | 482.6
22 | XS | 533.4
24 | XS | 584.2
26 | XS | 635
28 | XS | 685.8
30 | XS | 736.6
32 | XS | 787.4
36 | XS | 889
42 | XS | 1041.4
48 | XS | 1193.8
0.5 | XXS | 6.3
0.75 | XXS | 11.1
1 | XXS | 15.2
1.25 | XXS | 22.8
1.5 | XXS | 27.9
2 | XXS | 38.1
2.5 | XXS | 45
3 | XXS | 58.5
4 | XXS | 80.1
5 | XXS | 103.1
6 | XXS | 124.5
8 | XXS | 174.7
10 | XXS | 222.3
12 | XXS | 273.1
14 | SCH10 | 342.9
16 | SCH10 | 393.7
18 | SCH10 | 444.5
20 | SCH10 | 495.3
22 | SCH10 | 546.1
24 | SCH10 | 596.9
26 | SCH10 | 644.56
28 | SCH10 | 695.36
30 | SCH10 | 746.16
32 | SCH10 | 796.96
36 | SCH10 | 898.56
8 | SCH20 | 206.3
10 | SCH20 | 260.3
12 | SCH20 | 311.1
14 | SCH20 | 339.76
16 | SCH20 | 390.56
18 | SCH20 | 441.36
20 | SCH20 | 488.94
22 | SCH20 | 539.74
24 | SCH20 | 590.54
26 | SCH20 | 635
28 | SCH20 | 685.8
30 | SCH20 | 736.6
32 | SCH20 | 787.4
36 | SCH20 | 889
8 | SCH30 | 205.1
10 | SCH30 | 257.5
12 | SCH30 | 307.1
14 | SCH30 | 336.54
16 | SCH30 | 387.34
18 | SCH30 | 434.94
20 | SCH30 | 482.6
22 | SCH30 | 533.4
24 | SCH30 | 581.06
26 | SCH30 | 628.64
28 | SCH30 | 679.44
30 | SCH30 | 730.24
32 | SCH30 | 781.04
36 | SCH30 | 882.64
0.125 | SCH40 | 6.84
0.25 | SCH40 | 9.22
0.375 | SCH40 | 11.56
0.5 | SCH40 | 15.7
0.75 | SCH40 | 20.9
1 | SCH40 | 26.6
1.25 | SCH40 | 35
1.5 | SCH40 | 40.9
2 | SCH40 | 52.5
2.5 | SCH40 | 62.6
3 | SCH40 | 77.9
3.5 | SCH40 | 90.2
4 | SCH40 | 102.3
5 | SCH40 | 128.1
6 | SCH40 | 154.1
8 | SCH40 | 202.7
10 | SCH40 | 254.5
12 | SCH40 | 303.3
14 | SCH40 | 333.34
16 | SCH40 | 381
18 | SCH40 | 428.66
20 | SCH40 | 477.82
24 | SCH40 | 574.64
32 | SCH40 | 777.84
36 | SCH40 | 876.3
8 | SCH60 | 198.5
10 | SCH60 | 247.7
12 | SCH60 | 295.3
14 | SCH60 | 325.42
16 | SCH60 | 373.08
18 | SCH60 | 419.1
20 | SCH60 | 466.76
22 | SCH60 | 514.34
24 | SCH60 | 560.38
0.125 | SCH80 | 5.48
0.25 | SCH80 | 7.66
0.375 | SCH80 | 10.7
0.5 | SCH80 | 13.9
0.75 | SCH80 | 18.9
1 | SCH80 | 24.4
1.25 | SCH80 | 32.4
1.5 | SCH80 | 38.1
2 | SCH80 | 49.3
2.5 | SCH80 | 59
3 | SCH80 | 73.7
3.5 | SCH80 | 85.4
4 | SCH80 | 97.1
5 | SCH80 | 122.3
6 | SCH80 | 146.3
8 | SCH80 | 193.7
10 | SCH80 | 242.9
12 | SCH80 | 288.9
14 | SCH80 | 317.5
16 | SCH80 | 363.52
18 | SCH80 | 409.54
20 | SCH80 | 455.62
22 | SCH80 | 501.6
24 | SCH80 | 547.68
8 | SCH100 | 188.9
10 | SCH100 | 236.5
12 | SCH100 | 281.1
14 | SCH100 | 307.94
16 | SCH100 | 354.02
18 | SCH100 | 398.48
20 | SCH100 | 442.92
24 | SCH100 | 531.82
4 | SCH120 | 92.1
5 | SCH120 | 115.9
6 | SCH120 | 139.7
8 | SCH120 | 182.5
10 | SCH120 | 230.3
12 | SCH120 | 273.1
14 | SCH120 | 300.02
16 | SCH120 | 344.48
18 | SCH120 | 387.36
20 | SCH120 | 431.8
24 | SCH120 | 517.56
8 | SCH140 | 177.9
10 | SCH140 | 222.3
12 | SCH140 | 266.7
14 | SCH140 | 292.1
16 | SCH140 | 333.36
18 | SCH140 | 377.82
20 | SCH140 | 419.1
24 | SCH140 | 504.82
0.5 | SCH160 | 11.7
0.75 | SCH160 | 15.5
1 | SCH160 | 20.6
1.25 | SCH160 | 29.4
1.5 | SCH160 | 34.1
2 | SCH160 | 42.9
2.5 | SCH160 | 54
3 | SCH160 | 66.7
4 | SCH160 | 87.3
5 | SCH160 | 109.5
6 | SCH160 | 131.7
8 | SCH160 | 173.1
10 | SCH160 | 215.9
12 | SCH160 | 257.3
14 | SCH160 | 284.18
16 | SCH160 | 325.42
18 | SCH160 | 366.72
20 | SCH160 | 407.98
24 | SCH160 | 490.52

## schedList
Schedule
STD
XS
XXS
SCH10
SCH20
SCH30
SCH40
SCH60
SCH80
SCH100
SCH120
SCH140
SCH160

## npsList
NPS
0.125
0.25
0.375
0.5
0.75
1
1.25
1.5
2
2.5
3
3.5
4
5
6
8
10
12
14
16
18
20
22
24
26
28
30
32
36
42
48